Turbo-Lux® 3 Digital

Information in advance for the planning company

The following tender text should serve as an aid in the preparation of tender specifications.

We ask you to clearly mark your selected options and to delete the options you do not want.

BIM / CAD data (revit, dwg, stp format) of the devices are available!

https://www.mecon.de/en/orifice-flow-meters/turbo-lux-3-digital/#tabs1-3

Orifice plate flowmeter with grooved connection DN 50 … DN 300 used to measure the volume of water in closed conduits FM approved.

The orifice plate flowmeter consists of an orifice plate for stationary installation and a portable digital bypass meter (any installation position and flow direction).

Version

Standard version for inlet path 5 x D and outflow zone 2 x D with calibration certificate of bypass meter.

Installation lengths

DN 50 (2”) … DN 100 (4”):	100 mm (+0/-2 mm)
DN 150 (6”) … DN 300 (12”):	200 mm (+0/-3 mm)

Approvals

FM Approval Class 1046

Application conditions

Temperature limit: 	4 °C … 50 °C (39 °F … 122 °F)

Pressure limit: 	34.5 bar (500 psi), DN 50 (2“) … DN 200 (8“) - FM
	16 bar (232 psi), DN 250 (10“) … DN 300 (12“) - FM

Hydrostatically strength	64 bar (928 psi) for 5 min. (FM)
/ Pressure strength:

Bypass meter

Order Code	TL3D0

Measuring range

| Order Code | Nominal Size |  | Diameter | Flow Range | Flow Range |
| --- | --- | --- | --- | --- | --- |
|  |  |  | (mm) | (USgpm) | (lpm) |
| TL3P0-EB | 2"/ DN 50 |  | 60.3 | 20 … 100 | 75 … 375 |
| TL3P0-UC |  | 2½"/ DN 65 | 73.0 | 40 … 200 | 150 … 750 |
| TL3P0-FC |  | 2½"/ DN 65 | 76.1 | 40 … 200 | 150 … 750 |
| TL3P0-GD |  | 3"/ DN 80 | 88.9 | 60 … 300 | 220 … 1 100 |
| TL3P0-GE |  | 3"/ DN 80 | 88.9 | 80 … 400 | 300 … 1 500 |
| TL3P0-HF |  | 4"/ DN 100 | 114.3 | 100 … 500 | 380 … 1 900 |
| TL3P0-HG |  | 4"/ DN 100 | 114.3 | 120 … 600 | 460 … 2 300 |
| TL3P0-HH |  | 4"/ DN 100 | 114.3 | 160 … 800 | 600 … 3 000 |
| TL3P0-HJ |  | 4"/ DN 100 | 114.3 | 180 … 900 | 680 … 3 400 |
| TL3P0-XK |  | 6"/ DN 150 | 165.1 | 200 … 1 000 | 760 … 3 800 |
| TL3P0-XL |  | 6"/ DN 150 | 165.1 | 300 … 1 500 | 1 130 … 5 650 |
| TL3P0-XM |  | 6"/ DN 150 | 165.1 | 400 … 2 000 | 1 500 … 7 500 |
| TL3P0-XN |  | 6"/ DN 150 | 165.1 | 500 … 2 500 | 1 900 … 9 500 |
| TL3P0-KK |  | 6"/ DN 150 | 168.3 | 200 … 1.000 | 760 … 3 800 |
| TL3P0-KL |  | 6"/ DN 150 | 168.3 | 300 … 1 500 | 1 130 … 5 650 |
| TL3P0-KM |  | 6"/ DN 150 | 168.3 | 400 … 2 000 | 1 500 … 7 500 |
| TL3P0-KN |  | 6"/ DN 150 | 168.3 | 500 … 2 500 | 1 900 … 9 500 |
| TL3P0-LP |  | 8"/ DN 200 | 219.1 | 600 … 3.000 | 2 200 … 11 000 |
| TL3P0-LQ |  | 8"/ DN 200 | 219.1 | 800 … 4 000 | 3 000 … 15 000 |
| TL3P0-LR |  | 8"/ DN 200 | 219.1 | 1 000 … 5 000 | 3 800 … 19 000 |
| TL3P0-LS |  | 8"/ DN 200 | 219.1 | 1 200 … 6 000 | 4 500 … 22 500 |
| TL3P0-MT |  | 10"/ DN 250 | 273.0 | 1 400 … 7 000 | 5 300 … 26 500 |
| TL3P0-MU |  | 10"/ DN 250 | 273.0 | 1 600 … 8 000 | 6 000 … 30 000 |
| TL3P0-MV |  | 10"/ DN 250 | 273.0 | 1 800 … 9 000 | 6 800 … 34 000 |
| TL3P0-NW |  | 12"/ DN 300 | 323.9 | 2 000 … 10 000 | 7 600 … 38 000 |

Accessories (optional)

Description 	Order code

5 m connection cable
(to connect this to your PLC or pump controller)	ZB-TL3D0-001

Round connector socket 4-pole	ZB-TL3D0-004

Plug-in power supply unit 1,5 m Typ C (CEE)	ZB-TL3D0-002

Plug-in power supply 1,5 m Typ GB	ZB-TL3D0-005

Brand: 	MECON GmbH or equivalent

Typ: 	Turbo-Lux® 3 Digital

CAD data of the devices are available!

Point of contact - customer service: +49 (0)2237 60006-0, info@mecon.de