Turbo-Lux® 3

Information in advance for the planning company

The following tender text should serve as an aid in the preparation of tender specifications.

We ask you to clearly mark your selected options and to delete the options you do not want.

BIM / CAD data (revit, dwg, stp format) of the devices are available!

https://www.mecon.de/en/orifice-flow-meters/turbo-lux-3/#tabs1-3

Orifice plate flowmeter with grooved connection DN 50 … DN 300 used to measure the volume of water in closed conduits FM, LPCB and VdS approved.

The orifice plate flowmeter consists of an orifice plate for stationary installation and a portable bypass meter (any installation position and flow direction).

Version

Standard version for inlet path 5 x D and outflow zone 2 x D with calibration certificate for bypass meter.

Installation lengths

DN 50 (2”) … DN 100 (4”):	100 mm (+0/-2 mm)

DN 150 (6”) … DN 300 (12”):	200 mm (+0/-3 mm)

Approvals

FM Approval Class 1046
LPCB Approval LPS 1045
VdS-Approval 2344; 2100-29

Application conditions

Temperature limit: 	4 °C … 50 °C (39 °F … 122 °F)

Pressure limit: 	34.5 bar (500 psi), DN 50 (2“) … DN 200 (8“) - FM
	16 bar (232 psi), DN 250 (10“) … DN 300 (12“) - FM
	16 bar (232 psi), DN 50 (2“) … DN 200 (8“) - LPCB, VdS

Hydrostatically strength	64 bar (928 psi) for 5 min. (FM)
/ Pressure strength:	40 bar (580 psi) for 5 min. (LPCB)
	64 bar (928 psi) for 10 min. (VdS)

Measuring range

| Order Code | Nominal Size |  | Diameter | Flow Range | Flow Range |
| --- | --- | --- | --- | --- | --- |
|  |  |  | (mm) | (USgpm) | (lpm) |
| TL3A0-EB | 2"/ DN 50 |  | 60.3 | 20 … 100 | 75 … 375 |
| TL3A0-UC* |  | 2½"/ DN 65 | 73.0 | 40 … 200 | 150 … 750 |
| TL3A0-FC |  | 2½"/ DN 65 | 76.1 | 40 … 200 | 150 … 750 |
| TL3A0-GD |  | 3"/ DN 80 | 88.9 | 60 … 300 | 220 … 1 100 |
| TL3A0-GE |  | 3"/ DN 80 | 88.9 | 80 … 400 | 300 … 1 500 |
| TL3A0-HF |  | 4"/ DN 100 | 114.3 | 100 … 500 | 380 … 1 900 |
| TL3A0-HG |  | 4"/ DN 100 | 114.3 | 120 … 600 | 460 … 2 300 |
| TL3A0-HH |  | 4"/ DN 100 | 114.3 | 160 … 800 | 600 … 3 000 |
| TL3A0-HJ |  | 4"/ DN 100 | 114.3 | 180 … 900 | 680 … 3 400 |
| TL3A0-XK |  | 6"/ DN 150 | 165.1 | 200 … 1 000 | 760 … 3 800 |
| TL3A0-XL |  | 6"/ DN 150 | 165.1 | 300 … 1 500 | 1 130 … 5 650 |
| TL3A0-XM |  | 6"/ DN 150 | 165.1 | 400 … 2 000 | 1 500 … 7 500 |
| TL3A0-XN |  | 6"/ DN 150 | 165.1 | 500 … 2 500 | 1 900 … 9 500 |
| TL3A0-KK |  | 6"/ DN 150 | 168.3 | 200 … 1.000 | 760 … 3 800 |
| TL3A0-KL |  | 6"/ DN 150 | 168.3 | 300 … 1 500 | 1 130 … 5 650 |
| TL3A0-KM |  | 6"/ DN 150 | 168.3 | 400 … 2 000 | 1 500 … 7 500 |
| TL3A0-KN |  | 6"/ DN 150 | 168.3 | 500 … 2 500 | 1 900 … 9 500 |
| TL3A0-LP |  | 8"/ DN 200 | 219.1 | 600 … 3.000 | 2 200 … 11 000 |
| TL3A0-LQ |  | 8"/ DN 200 | 219.1 | 800 … 4 000 | 3 000 … 15 000 |
| TL3A0-LR |  | 8"/ DN 200 | 219.1 | 1 000 … 5 000 | 3 800 … 19 000 |
| TL3A0-LS** |  | 8"/ DN 200 | 219.1 | 1 200 … 6 000 | 4 500 … 22 500 |
| TL3A0-MT* |  | 10"/ DN 250 | 273.0 | 1 400 … 7 000 | 5 300 … 26 500 |
| TL3A0-MU* |  | 10"/ DN 250 | 273.0 | 1 600 … 8 000 | 6 000 … 30 000 |
| TL3A0-MV* |  | 10"/ DN 250 | 273.0 | 1 800 … 9 000 | 6 800 … 34 000 |
| TL3A0-NW* |  | 12"/ DN 300 | 323.9 | 2 000 … 10 000 | 7 600 … 38 000 |

*FM approved

**VdS-limited flow range up to 10 m/s (corresponds to 20 800 lpm)

Brand: 	MECON GmbH or equivalent

Typ: 	Turbo-Lux® 3

CAD data of the devices are available!

Point of contact - customer service: +49 (0)2237 60006-0, info@mecon.de