Turbo-Lux®

Information in advance for the planning company

The following tender text should serve as an aid in the preparation of tender specifications.

We ask you to clearly mark your selected options and to delete the options you do not want.

CAD data (dwg, stp format) of the devices are available at:

https://www.mecon.de/en/orifice-flow-meters/turbo-lux/#tabs1-3

Orifice plate flowmeter for installation between flanges DN 80 … DN 250 used to measure the volume of water in closed conduits VdS approved.

The orifice plate flowmeter consists of an orifice plate for stationary installation and a portable bypass meter (any installation position and flow direction) – optional with calibration certificate.

Version

Standard version for inlet path 10 x D and outflow zone 5 x D.

Approvals

VdS-Approval Class 2344; 2100-29

Application conditions

Temperature limit:	4 °C … 50 °C
	(39 °F … 122 °F)

Pressure limit:	max. 12 bar

Bypass meter (display part)	Order code

without calibration certificate 	7ME5830-0AB00-0AA0

with calibration certificate 	7ME5830-0AB00-1AA0

Orifice plate

DN 80 … DN 250 for installation between flanges

Nominal size	Flow range	Order code

DN 80 (3“)	Qv: 0,42 … 2,1 m3/min	7ME5834-1AB00-0AA0

DN 100 (4“)	Qv: 0,60 … 3,0 m3/min	7ME5834-2AB00-0AA0

DN 150 (6“)	Qv: 1,20 … 6,0 m3/min	7ME5834-3AB00-0AA0

DN 200 (8“)	Qv: 2,40 … 12,0 m3/min	7ME5834-4AB00-0AA0

DN 250 (10“)	Qv: 3,60 … 18,0 m3/min	7ME5834-5AB00-0AA0

Centering assembly (for installation between flanges - optional)

Nominal size	Order code

DN 80 (3”)	7ME5834-0BA00-0AA0

DN 100 (4”)	7ME5834-0CA00-0AA0

DN 150 (6”)	7ME5834-0EA00-0AA0

DN 200 (8”) - 10 PN	7ME5834-0FA00-0AA0

DN 200 (8”) - 16 PN	7ME5834-0KA00-0AA0

DN 250 (10”)	7ME5834-0GA00-0AA0

Case for storage (bypass meter - optional)

Order code: 7ME5830-0AA10-0AA0

Brand: MECON GmbH - or equivalent

Typ: Turbo-Lux®

CAD data of the devices are available!

Point of contact - customer service: +49 (0)2237 60006-0, info@mecon.de